## Calculation
Heat Pump Sizing Guide
Prepared for:
Date:
Step 1 | Select (nearest) Location |  | Melbourne
Step 2 | Enter Swimming Pool Dimensions |  | Metres
|  | Average Length | 10
|  | Average Width | 5
|  | Average Depth | 1.5
|  | Litres | 75000
Step 3 | Enter Desired Swimming Temperature |  | 28
[5 empty] | No Cover | With Cover
Step 4 | Select your type of Swimming Season |  | All Year Round |  | kW | kW
|  |  | Jan to Dec | Jan | 687.3 | 412.38
|  | kW Required to Raise Water Temperature |  | Feb | 713.4 | 428.04
|  |  |  | Mar | 904.8 | 542.88
|  |  |  | Apr | 1165.8 | 699.48
|  |  |  | May | 1461.6 | 876.96
|  |  |  | Jun | 1653 | 991.8
|  |  |  | Jul | 1722.6 | 1033.56
|  |  |  | Aug | 1609.5 | 965.7
|  |  |  | Sep | 1400.7 | 840.42
|  |  |  | Oct | 1165.8 | 699.48
|  |  |  | Nov | 1000.5 | 600.3
|  |  |  | Dec | 826.5 | 495.9
| Recommended Heat Pump Model ** |  |  | Standard Heat Pump 47.0 KW Commercial
| Recommended Heat Pump Model (With Cover) ** |  |  | Viron Inverter Heat Pump iHP283
** Recommended model is based on heat maintenance only. Additional time or kW required for initial / start of season heat up of your pool or spa
Heating Cost
Step 5 | Enter Power Cost (cents per kW hour) |  | 28
[5 empty] | No Cover | With Cover
|  |  |  | Jan | 40.0925 | 23.0933
| Heat Up Cost |  |  | Feb | 41.615 | 23.9702
| (in month on initial heat up) |  |  | Mar | 52.78 | 30.4013
|  |  |  | Apr | 68.005 | 39.1709
|  |  |  | May | 102.312 | 61.3872
|  |  |  | Jun | 115.71 | 69.426
|  |  |  | Jul | 120.582 | 72.3492
|  |  |  | Aug | 112.665 | 67.599
|  |  |  | Sep | 98.049 | 58.8294
|  |  |  | Oct | 68.005 | 39.1709
|  |  |  | Nov | 58.3625 | 33.6168
|  |  |  | Dec | 48.2125 | 27.7704
[5 empty] | No Cover | With Cover
|  |  |  | Jan | 11.5466 | 6.928
| Daily Cost to maintain Temperature |  |  | Feb | 11.9851 | 7.1911
|  |  |  | Mar | 15.2006 | 9.1204
|  |  |  | Apr | 19.5854 | 11.7513
|  |  |  | May | 30.6936 | 18.4162
|  |  |  | Jun | 34.713 | 20.8278
|  |  |  | Jul | 36.1746 | 21.7048
|  |  |  | Aug | 33.7995 | 20.2797
|  |  |  | Sep | 29.4147 | 17.6488
|  |  |  | Oct | 19.5854 | 11.7513
|  |  |  | Nov | 16.8084 | 10.085
|  |  |  | Dec | 13.8852 | 8.3311
|  |  |  | Annual Total | 7388.0957 | 4432.8574
**** | Avg. temperature rise per hour at ambient condition 1: |  |  |  | 0.45004 | degrees
| Avg. temperature rise per hour at ambient condition 2: |  |  |  | 0.45004 | degrees
Notes:
**** | Ambient Condition 1 is 24 degree air temperature, 63% RH & 27 degree entering water temperature
Ambient Condition 1 is 10 degree air temperature, 63% RH & 27 degree entering water temperature
Enter Data into Bluefields
Step 1 | Enter Nearest Location or location with similar weather conditions
Step 3 | Comfortable swimming temperature is 26-28 degrees.
Step 4 | Solar alternative season is from October - March, Extended season is from Sept-April, All rear round is all year round.
Step 5 | Peak Tarrif Electricity is generally approximatley 22-28 cents per kW hour
******Note***** This sizing guide is indicative only. In general, heat pumps are recommended replace or support solar heating or extend the swimming season to 8 or 9 months a year.
The use of a thermal blanket may reduce operating costs by up to 40% however, as many pool owners leave the blanket off during
the swimming season, these calculations assume that no blanket is used and the size of the heat pump is calculated also without a cover being used.
If swimming is required all year round, or you are selecting for a commercial establishment that requires a guarranteed temperature all
year round AstralPool recommend the use or a back up gas fired Heater.
Always consult your nearest AstralPool office when sizing heating for a commercial establishment.
A Division of
Note on H25: Internal Note Only: 16% = kW gross up factor to calculate total Kw needed to heat a set volume of water (i.e. 1000 litre of water takes 1000*1.16 kW x temperature gap)

## Temperatures
Desired Temp | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
| 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | City selection
City | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec
Adelaide | 23.1 | 22.6 | 20.4 | 17.6 | 13.7 | 11.4 | 10.4 | 11.3 | 13.8 | 16.8 | 19.1 | 20.8 | 0
Brisbane | 25.6 | 25.3 | 23.8 | 21.5 | 17.6 | 14.8 | 13.5 | 15.4 | 18.8 | 21.9 | 23.9 | 25.1 | 0
Melbourne | 20.1 | 19.8 | 17.6 | 14.6 | 11.2 | 9 | 8.2 | 9.5 | 11.9 | 14.6 | 16.5 | 18.5 | 1
Perth | 23.9 | 23.4 | 21.2 | 17.9 | 15.2 | 13.3 | 11.9 | 12.6 | 14.5 | 17.3 | 20 | 22.7 | 0
Sydney | 22.9 | 23 | 21.4 | 18.4 | 14.3 | 12 | 10.9 | 12.5 | 15.4 | 18.6 | 20.7 | 22.1 | 0
Townsville | 25.6 | 25.3 | 23.8 | 23.5 | 20.6 | 17.8 | 16.5 | 18.4 | 21.8 | 24.9 | 25.9 | 27.1 | 0
Tasmania | 18 | 18 | 16 | 14 | 11 | 9 | 8 | 10 | 11 | 13 | 15 | 17 | 0
Graph data - Unheated water | 20.1 | 19.8 | 17.6 | 14.6 | 11.2 | 9 | 8.2 | 9.5 | 11.9 | 14.6 | 16.5 | 18.5
Desired temp less City Avg Temp | 7.9 | 8.2 | 10.4 | 13.4 | 16.8 | 19 | 19.8 | 18.5 | 16.1 | 13.4 | 11.5 | 9.5
** Row 15 & 16 are now irrelevant **
Desired temp less City Avg Temp | 4.9 | 5.4 | 7.6 | 10.4 | 14.3 | 10.2 | 17.6 | 16.7 | 14.2 | 11.2 | 8.9 | 7.2
| -5.1 | -4.6 | -2.4 | 0.4 | 4.3 | 0.2 | 7.6 | 6.7 | 4.2 | 1.2 | -1.1 | -2.8
Achieved Water Temp - Extended Season
Adelaide | 28 | 28 | 28 | 28 | 13.7 | 11.4 | 10.4 | 11.3 | 28 | 28 | 28 | 28
Brisbane | 28 | 28 | 28 | 28 | 17.6 | 14.8 | 13.5 | 15.4 | 28 | 28 | 28 | 28
Melbourne | 28 | 28 | 28 | 28 | 11.2 | 9 | 8.2 | 9.5 | 28 | 28 | 28 | 28
Perth | 28 | 28 | 28 | 28 | 15.2 | 13.3 | 11.9 | 12.6 | 28 | 28 | 28 | 28
Sydney | 28 | 28 | 28 | 28 | 14.3 | 12 | 10.9 | 12.5 | 28 | 28 | 28 | 28
Townsville | 28 | 28 | 28 | 28 | 20.6 | 17.8 | 16.5 | 18.4 | 28 | 28 | 28 | 28
Tasmania | 28 | 28 | 28 | 28 | 11 | 9 | 8 | 10 | 28 | 28 | 28 | 28
Achieved Water Temp - Year Round Season
Adelaide | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Brisbane | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Melbourne | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Perth | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Sydney | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Townsville | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Tasmania | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Achieved Water Temp - Solar Alternative
Adelaide | 28 | 28 | 28 | 17.6 | 13.7 | 11.4 | 10.4 | 11.3 | 13.8 | 28 | 28 | 28
Brisbane | 28 | 28 | 28 | 21.5 | 17.6 | 14.8 | 13.5 | 15.4 | 18.8 | 28 | 28 | 28
Melbourne | 28 | 28 | 28 | 14.6 | 11.2 | 9 | 8.2 | 9.5 | 11.9 | 28 | 28 | 28
Perth | 28 | 28 | 28 | 17.9 | 15.2 | 13.3 | 11.9 | 12.6 | 14.5 | 28 | 28 | 28
Sydney | 28 | 28 | 28 | 18.4 | 14.3 | 12 | 10.9 | 12.5 | 15.4 | 28 | 28 | 28
Townsville | 28 | 28 | 28 | 23.5 | 20.6 | 17.8 | 16.5 | 18.4 | 21.8 | 28 | 28 | 28
Tasmania | 28 | 28 | 28 | 14 | 11 | 9 | 8 | 10 | 11 | 28 | 28 | 28
Graph data - Achievable Water Temp | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28 | 28
Monthly Cost to Heat
|  | No Cover | With Cover
| Jan | 357.9458 | 214.7675
| Feb | 335.5834 | 222.9232
| Mar | 471.2198 | 282.7319
| Apr | 587.5632 | 364.2892
| May | 951.5016 | 570.901
| Jun | 1041.39 | 645.6618
| Jul | 1121.4126 | 672.8476
| Aug | 1047.7845 | 628.6707
| Sep | 911.8557 | 547.1134 | hurl
| Oct | 587.5632 | 364.2892
| Nov | 521.0604 | 312.6362
| Dec | 430.4412 | 258.2647

## Model selection
Indication | 47.3715 |  |  |  |  | Indication | 28.4229
| Heat Pump - No Cover | [5 empty] | Heat Pump - Cover
| Extended Season | All Year Round | Extended selection | All Year selection |  |  | Extended Season | All Year Round | Extended selection | All Year selection
Phase | kw output cond'n 1 | kw output cond'n 2 |  |  | Model | Phase | kw output cond'n 1 | kw output cond'n 2 |  |  | Model
Single | 9.5333 | 9.5333 | 0 | 0 | Inverter Heat Pump ECO iHP70, Inverter Heat Pump ECO iHP90 or Viron Inverter Heat Pump iHP90 | Single | 9.5333 | 9.5333 | 0 | 0 | Inverter Heat Pump ECO iHP70, Inverter Heat Pump ECO iHP90 or Viron Inverter Heat Pump iHP90
Single | 13.65 | 13.65 | 0 | 0 | Inverter Heat Pump ECO iHP120 or Viron Inverter Heat Pump iHP120 or Inverter Heat Pump Top iHPT127 | Single | 13.65 | 13.65 | 0 | 0 | Inverter Heat Pump ECO iHP120 or Viron Inverter Heat Pump iHP120 or Inverter Heat Pump Top iHPT127
Single | 13.65 | 13.65 | 0 | 0 | Inverter Heat Pump ECO iHP120 or Viron Inverter Heat Pump iHP120 or Inverter Heat Pump Top iHPT127 | Single | 13.65 | 13.65 | 0 | 0 | Inverter Heat Pump ECO iHP120 or Viron Inverter Heat Pump iHP120 or Inverter Heat Pump Top iHPT127
Single | 18.4167 | 18.4167 | 0 | 0 | Viron Inverter Heat Pump iHP170 or Inverter Heat Pump Top iHPT168 | Single | 18.4167 | 18.4167 | 0 | 0 | Viron Inverter Heat Pump iHP170 or Inverter Heat Pump Top iHPT168
Single | 21.125 | 21.125 | 0 | 0 | Viron Inverter Heat Pump iHP195 | Single | 21.125 | 21.125 | 0 | 0 | Viron Inverter Heat Pump iHP195
Single | 26.2167 | 26.2167 | 0 | 0 | Viron Inverter Heat Pump iHP242 or Inverter Heat Pump Top iHPT246 | Single | 26.2167 | 26.2167 | 0 | 0 | Viron Inverter Heat Pump iHP242 or Inverter Heat Pump Top iHPT246
Three | 30.6583 | 30.6583 | 0 | 0 | Viron Inverter Heat Pump iHP283 | Three | 30.6583 | 30.6583 | 1 | 1 | Viron Inverter Heat Pump iHP283
Three | 50.9 | 50.9 | 1 | 1 | Standard Heat Pump 47.0 KW Commercial | Three | 50.9 | 50.9 | 1 | 1 | Standard Heat Pump 47.0 KW Commercial
Three | 62.8 | 62.8 | 0 | 0 | Standard Heat Pump 58.0 KW Commercial | Three | 62.8 | 62.8 | 1 | 1 | Standard Heat Pump 58.0 KW Commercial
Three | 102.9 | 102.9 | 0 | 0 | Standard Heat Pump 95.0 KW Commercial | Three | 102.9 | 102.9 | 1 | 1 | Standard Heat Pump 95.0 KW Commercial
Three | 130 | 130 | 0 | 0 | Standard Heat Pump 120.0 KW Commercial | Three | 130 | 130 | 1 | 1 | Standard Heat Pump 120.0 KW Commercial
Three | 157.1 | 157.1 | 0 | 0 | Standard Heat Pump 145.0 KW Commercial | Three | 157.1 | 157.1 | 1 | 1 | Standard Heat Pump 145.0 KW Commercial
Three | 238.3 | 238.3 | 0 | 0 | Standard Heat Pump 220.0 KW Commercial | Three | 238.3 | 238.3 | 1 | 1 | Standard Heat Pump 220.0 KW Commercial
Note on B1: Adam Jaworski: 1. Maximum kW required to increase pool temperature from ambient to desired temperature 2. Multiply by 33% - this represents the kW required to make up the 33% daily heat loss from the pool 3. Multiply by 12 hours - this is the industry standard accepted running time Daily kW Req'd = Maximum Heat Up kW required x 33% x 12 hours
Note on H1: Adam Jaworski: 1. Maximum kW required to increase pool temperature from ambient to desired temperature 2. Multiply by 33% - this represents the kW required to make up the 33% daily heat loss from the pool 3. Multiply by 12 hours - this is the industry standard accepted running time Daily kW Req'd = Maximum Heat Up kW required x 33% x 12 hours

## Preus
Product Code | Prodcuct Description | Price List
78566 | Inverter Heat Pump ECO IHP70 | 3925
78567 | Inverter Heat Pump ECO IHP90 | 4086
78568 | Inverter Heat Pump ECO IHP120 | 4818
78542 | Viron Inverter Heat Pump iHP90 | 6076
78543 | Viron Inverter Heat Pump iHP120 | 7124
78544 | Viron Inverter Heat Pump iHP170 | 9430
78545 | Viron Inverter Heat Pump iHP195 | 10476
78546 | Viron Inverter Heat Pump iHP242 | 12570
78547 | Viron Inverter Heat Pump iHP283 | 13624
78560 | Inverter Heat Pump Top iHPT127 | 7236
78561 | Inverter Heat Pump Top iHPT168 | 9542
78562 | Inverter Heat Pump Top iHPT246 | 12562
78550 | AstralPool 47.0 KW Commercial | 19290
78551 | AstralPool 58.0 KW Commercial | 21024
78552 | AstralPool 95.0 KW Commercial | 29116
78553 | AstralPool 120.0 KW Commercial | 38954
78554 | AstralPool 145.0 KW Commercial | 48572
78555 | AstralPool 220.0 KW Commercial | 60274